## 56 MLd indrapuram
OM & M Cell, Directorate of Urban Bodies, Department of Urban Development, Government of Uttar Pradesh
Uttar Pradesh Jal Nigam, Ghaziabad
VA TECH WABAG LIMITED
MONTHLY LAB REPORT
Name of the plant |  |  |  | STP Indirapuram, Ghaziabad | [5 empty] | Technology | [5 empty] | UASB based
Capacity |  |  |  | 56 MLD | [5 empty] | Month | [5 empty] | 2021-11-01
Date | Raw Sewage Flow | Raw Sewage Parameters | [5 empty] | Final Outlet Parameters | [7 empty] | Penalty applicability as per Office Memorandum dated: 01/01/2020 Point no :10 | Third Party/UPPCB Report | Remark
|  | pH | BOD | COD | TSS | DO | Industrial Effluent (Y/N) | pH | BOD | COD | TSS | DO | faecal coliform | OUTLET | SLUDGE GENERATION/DAY
|  | ---- | mg/L | mg/L | mg/L | mg/L |  | ---- | mg/L | mg/L | mg/L | mg/L | (MPN/100 ml)
Contract Parameter Mandatory | MLD | 6.5-8.0 | 200 | 400 | 450 | 0 |  | 7.0-7.5 | <30 | <100 | <50 | >4.5 - 5.0 |  | MLD | MTM
2021-11-01 | 25.49 | 7.22 | 190 | 378 | 316 | 0 | No | 7.28 | 21 | 60 | 31 | 2.7 | NA | 24.27 | 1.0196
2021-11-02 | 25.37 | 7.18 | 180 | 368 | 324 | 0 | No | 7.32 | 24 | 64 | 36 | 3.1 | NA | 24.17 | 1.0148
2021-11-03 | 25.93 | 7.16 | 185 | 352 | 336 | 0 | No | 7.25 | 22 | 74 | 39 | 2.8 | NA | 24.74 | 1.0372
2021-11-04 | 25.73 | 7.31 | 190 | 368 | 340 | 0 | No | 7.39 | 24 | 62 | 33 | 3.2 | NA | 24.58 | 1.0292
2021-11-05 | 25.36 | 7.2 | 180 | 384 | 352 | 0 | No | 7.36 | 26 | 76 | 36 | 3 | NA | 24.05 | 1.0144
2021-11-06 | 25.38 | 7.21 | 185 | 372 | 344 | 0 | No | 7.28 | 23 | 60 | 32 | 2.7 | NA | 24.05 | 1.0152
2021-11-07 | 25.63 | 7.16 | 160 | 346 | 292 | 0 | No | 7.25 | 20 | 58 | 28 | 2.9 | NA | 24.37 | 1.0252
2021-11-08 | 25.58 | 7.18 | 215 | 448 | 328 | 0 | No | 7.32 | 24 | 78 | 27 | 2.8 | NA | 24.27 | 1.0232
2021-11-09 | 25.37 | 7.22 | 210 | 422 | 312 | 0 | No | 7.29 | 21 | 70 | 30 | 2.7 | NA | 24.18 | 1.0148
2021-11-10 | 25.74 | 7.19 | 205 | 408 | 296 | 0 | No | 7.37 | 25 | 66 | 31 | 3.2 | NA | 24.48 | 1.0296
2021-11-11 | 25.47 | 7.23 | 180 | 362 | 304 | 0 | No | 7.35 | 23 | 74 | 29 | 2.9 | NA | 24.26 | 1.0188
2021-11-12 | 25.83 | 7.18 | 215 | 440 | 316 | 0 | No | 7.33 | 26 | 80 | 32 | 2.8 | NA | 24.69 | 1.0332
2021-11-13 | 25.73 | 7.22 | 205 | 422 | 296 | 0 | No | 7.31 | 24 | 76 | 28 | 3.1 | NA | 24.48 | 1.0292
2021-11-14 | 25.73 | 7.2 | 195 | 394 | 332 | 0 | No | 7.29 | 25 | 78 | 34 | 2.7 | NA | 24.51 | 1.0292
2021-11-15 | 25.53 | 7.17 | 210 | 424 | 320 | 0 | No | 7.26 | 23 | 72 | 30 | 2.5 | NA | 24.38 | 1.0212
2021-11-16 | 25.52 | 7.23 | 185 | 368 | 336 | 0 | No | 7.35 | 25 | 80 | 35 | 2.8 | NA | 24.27 | 1.0208
2021-11-17 | 25.27 | 7.18 | 220 | 436 | 312 | 0 | No | 7.28 | 27 | 84 | 29 | 2.6 | NA | 24.05 | 1.0108
2021-11-18 | 25.82 | 6.96 | 205 | 402 | 288 | 0 | No | 7.2 | 26 | 74 | 31 | 2.9 | NA | 24.62 | 1.0328
2021-11-19 | 25.18 | 7.2 | 185 | 386 | 308 | 0 | No | 7.33 | 24 | 66 | 36 | 2.7 | NA | 24.01 | 1.0072
2021-11-20 | 25.73 | 7.17 | 225 | 462 | 344 | 0 | No | 7.22 | 26 | 82 | 32 | 3.1 | NA | 24.37 | 1.0292
2021-11-21 | 25.18 | 7.21 | 215 | 440 | 328 | 0 | No | 7.27 | 23 | 78 | 28 | 3.2 | NA | 24.01 | 1.0072
2021-11-22 | 25.92 | 7.23 | 210 | 428 | 320 | 0 | No | 7.29 | 27 | 86 | 39 | 2.8 | NA | 24.73 | 1.0368
2021-11-23 | 25.02 | 7.2 | 230 | 456 | 340 | 0 | No | 7.26 | 25 | 72 | 33 | 3 | NA | 23.02 | 1.0008
2021-11-24 | 25.92 | 6.92 | 205 | 410 | 316 | 0 | No | 6.98 | 27 | 76 | 31 | 2.9 | NA | 24.73 | 1.0368
2021-11-25 | 25.36 | 7.19 | 180 | 358 | 324 | 0 | No | 7.25 | 24 | 68 | 27 | 3.2 | NA | 24.18 | 1.0144
2021-11-26 | 25.73 | 7.14 | 170 | 342 | 308 | 0 | No | 7.21 | 22 | 60 | 30 | 3 | NA | 24.51 | 1.0292
2021-11-27 | 25.42 | 7.17 | 160 | 336 | 296 | 0 | No | 7.24 | 25 | 64 | 32 | 2.8 | NA | 24.16 | 1.0168
2021-11-28 | 25.38 | 7.12 | 170 | 348 | 312 | 0 | No | 7.29 | 24 | 70 | 29 | 3.3 | NA | 24.14 | 1.0152
2021-11-29 | 25.38 | 6.84 | 175 | 352 | 328 | 0 | No | 6.96 | 27 | 78 | 34 | 2.7 | NA | 24.16 | 1.0152
2021-11-30 | 25.97 | 7.21 | 165 | 346 | 320 | 0 | No | 7.28 | 26 | 72 | 30 | 2.5 | NA | 24.63 | 1.0388
Total | 766.67 | [13 empty] | 30.6668
OM & M Cell, Directorate of Urban Bodies, Department of Urban Development, Government of Uttar Pradesh
Uttar Pradesh Jal Nigam, Ghaziabad
VA TECH WABAG LIMITED
MONTHLY LAB REPORT
Name of the plant |  |  |  | STP Indirapuram, Ghaziabad | [5 empty] | Technology | [5 empty] | UASB based
Capacity |  |  |  | 56 MLD | [5 empty] | Month | [5 empty] | 2021-12-01
Date | Raw Sewage Flow | Raw Sewage Parameters | [5 empty] | Final Outlet Parameters | [7 empty] | Penalty applicability as per Office Memorandum dated: 01/01/2020 Point no :10 | Third Party/UPPCB Report | Remark
|  | pH | BOD | COD | TSS | DO | Industrial Effluent (Y/N) | pH | BOD | COD | TSS | DO | OUTLET | faecal coliform | Sludge Generation/Day
|  | ---- | mg/L | mg/L | mg/L | mg/L |  | ---- | mg/L | mg/L | mg/L | mg/L |  | (MPN/100 ml) | MTD
Contract Parameter Mandatory | MLD | 6.5-8.0 | 200 | 400 | 450 | 0 |  | 7.0-7.5 | <30 | <100 | <50 | >4.5 - 5.0 | MLD
2021-12-01 | 28.53 | 7.19 | 180 | 358 | 332 | 0 | No | 7.31 | 24 | 80 | 35 | 2.9 | 27.42 | NA | 0.8559
2021-12-02 | 30.17 | 7.14 | 240 | 482 | 324 | 0 | No | 7.29 | 28 | 86 | 37 | 2.6 | 27.03 | NA | 0.9051
2021-12-03 | 28.53 | 7.16 | 230 | 474 | 316 | 0 | No | 7.26 | 25 | 78 | 28 | 2.8 | 27.37 | NA | 0.8559
2021-12-04 | 28.91 | 7.24 | 245 | 484 | 320 | 0 | No | 7.28 | 23 | 68 | 31 | 2.5 | 27.74 | NA | 0.8673
2021-12-05 | 28.66 | 7.17 | 225 | 468 | 336 | 0 | No | 7.25 | 20 | 74 | 36 | 2.7 | 27.57 | NA | 0.8598
2021-12-06 | 30.64 | 7.2 | 240 | 490 | 328 | 0 | No | 7.29 | 22 | 70 | 27 | 2.9 | 27.52 | NA | 0.9192
2021-12-07 | 28.67 | 7.22 | 230 | 452 | 344 | 0 | No | 7.27 | 26 | 84 | 39 | 2.6 | 27.54 | NA | 0.8601
2021-12-08 | 30.53 | 6.97 | 210 | 418 | 352 | 0 | No | 7.24 | 23 | 66 | 30 | 2.8 | 27.49 | NA | 0.9159
2021-12-09 | 28.78 | 6.88 | 215 | 428 | 330 | 0 | No | 7.28 | 21 | 74 | 28 | 2.6 | 27.63 | NA | 0.8634
2021-12-10 | 28.79 | 6.8 | 195 | 390 | 312 | 0 | No | 7.25 | 25 | 68 | 32 | 2.9 | 27.58 | NA | 0.8637
2021-12-11 | 28.64 | 7.18 | 205 | 420 | 324 | 0 | No | 7.29 | 27 | 76 | 37 | 3 | 27.53 | NA | 0.8592
2021-12-12 | 28.74 | 7.1 | 215 | 432 | 356 | 0 | No | 7.24 | 28 | 84 | 34 | 2.8 | 27.62 | NA | 0.8622
2021-12-13 | 29.66 | 6.94 | 210 | 424 | 336 | 0 | No | 7.22 | 23 | 70 | 31 | 2.6 | 27.51 | NA | 0.8898
2021-12-14 | 28.17 | 7.1 | 235 | 466 | 364 | 0 | No | 7.25 | 26 | 82 | 38 | 3.1 | 26.95 | NA | 0.8451
2021-12-15 | 29.27 | 7.15 | 220 | 436 | 352 | 0 | No | 7.28 | 24 | 74 | 32 | 2.9 | 27.05 | NA | 0.8781
2021-12-16 | 28.04 | 7.19 | 210 | 420 | 368 | 0 | No | 7.24 | 27 | 86 | 39 | 2.7 | 26.86 | NA | 0.8412
2021-12-17 | 29.4 | 7.12 | 215 | 428 | 356 | 0 | No | 7.27 | 25 | 80 | 36 | 2.5 | 27.28 | NA | 0.882
2021-12-18 | 28.79 | 7.15 | 205 | 410 | 384 | 0 | No | 7.23 | 23 | 72 | 29 | 2.8 | 27.58 | NA | 0.8637
2021-12-19 | 29.04 | 6.9 | 195 | 394 | 360 | 0 | No | 7.29 | 26 | 70 | 33 | 2.9 | 26.87 | NA | 0.8712
2021-12-20 | 28.79 | 7.1 | 205 | 412 | 376 | 0 | No | 7.26 | 25 | 84 | 38 | 2.7 | 27.57 | NA | 0.8637
2021-12-21 | 29.75 | 7.16 | 210 | 424 | 388 | 0 | No | 7.23 | 23 | 76 | 31 | 2.8 | 27.58 | NA | 0.8925
2021-12-22 | 28.57 | 6.87 | 190 | 408 | 372 | 0 | No | 7.31 | 25 | 70 | 34 | 2.7 | 27.42 | NA | 0.8571
2021-12-23 | 28.78 | 7.1 | 180 | 386 | 348 | 0 | No | 7.28 | 24 | 74 | 39 | 2.5 | 27.59 | NA | 0.8634
2021-12-24 | 28.53 | 6.96 | 195 | 418 | 364 | 0 | No | 7.21 | 27 | 86 | 32 | 2.3 | 27.39 | NA | 0.8559
2021-12-25 | 29.04 | 6.9 | 215 | 436 | 380 | 0 | No | 7.23 | 28 | 90 | 41 | 2.1 | 26.84 | NA | 0.8712
2021-12-26 | 28.4 | 6.95 | 205 | 424 | 376 | 0 | No | 7.2 | 26 | 82 | 37 | 2 | 27.27 | NA | 0.852
2021-12-27 | 28.53 | 6.91 | 215 | 446 | 392 | 0 | No | 7.22 | 26 | 88 | 38 | 2.2 | 27.46 | NA | 0.8559
2021-12-28 | 28.17 | 7.12 | 205 | 428 | 412 | 0 | No | 7.25 | 24 | 80 | 42 | 2.1 | 26.94 | NA | 0.8451
2021-12-29 | 30.27 | 7.15 | 190 | 390 | 360 | 0 | No | 7.27 | 22 | 76 | 35 | 2.3 | 27.05 | NA | 0.9081
2021-12-30 | 28.74 | 7.18 | 205 | 406 | 372 | 0 | No | 7.24 | 20 | 70 | 33 | 2.2 | 27.35 | NA | 0.8622
2021-12-31 | 28.92 | 7.11 | 220 | 452 | 410 | 0 | No | 7.26 | 27 | 86 | 38 | 2.4 | 27.83 | NA | 0.8676
Total Flow (MLD) | 898.45 | [13 empty] | 26.9535
VA Tech Wabag | [9 empty] | UP Jal Nigam Ghaziabad
OM & M Cell, Directorate of Urban Bodies, Department of Urban Development, Government of Uttar Pradesh
Uttar Pradesh Jal Nigam, Ghaziabad
VA TECH WABAG LIMITED
MONTHLY LAB REPORT
Name of the plant |  |  |  | STP Indirapuram, Ghaziabad | [5 empty] | Technology
Capacity |  |  |  | 56 MLD | [5 empty] | Month
Date | Raw Sewage Flow | Raw Sewage Parameters | [5 empty] | Final Outlet Parameters | [7 empty] | Remark
|  | pH | BOD | COD | TSS | DO | Industrial Effluent (Y/N) | pH | BOD | COD | TSS | DO | OUTLET | Sewage Generation/Day
|  | ---- | mg/L | mg/L | mg/L | mg/L |  | ---- | mg/L | mg/L | mg/L | mg/L |  | MTM
Contract Parameter Mandatory | MLD | 6.5-8.0 | 200 | 400 | 450 | 0 |  | 7.0-7.5 | <30 | <100 | <50 | >4.5 - 5.0 | MLD
2022-01-01 | 28.84 | 7.1 | 215 | 440 | 424 | 0 | No | 7.22 | 28 | 88 | 39 | 1.9 | 27.54 | 0.8652
2022-01-02 | 28.44 | 6.92 | 220 | 432 | 396 | 0 | No | 7.24 | 24 | 76 | 35 | 2.2 | 27.27 | 0.8532
2022-01-03 | 28.64 | 7.14 | 215 | 458 | 410 | 0 | No | 7.21 | 26 | 82 | 34 | 2.4 | 27.59 | 0.8592
2022-01-04 | 28.79 | 7.1 | 205 | 426 | 388 | 0 | No | 7.27 | 22 | 74 | 37 | 2.1 | 27.54 | 0.8637
2022-01-05 | 28.91 | 6.95 | 210 | 418 | 376 | 0 | No | 7.26 | 25 | 80 | 31 | 2.3 | 27.62 | 0.8673
2022-01-06 | 28.66 | 6.9 | 195 | 412 | 384 | 0 | No | 7.25 | 21 | 72 | 35 | 2.2 | 27.37 | 0.8598
2022-01-07 | 28.4 | 6.92 | 220 | 436 | 412 | 0 | No | 7.21 | 26 | 78 | 38 | 2 | 27.18 | 0.852
2022-01-08 | 28.91 | 7.2 | 235 | 472 | 420 | 0 | No | 7.27 | 28 | 86 | 32 | 2.2 | 27.72 | 0.8673
2022-01-09 | 28.66 | 7.1 | 210 | 422 | 392 | 0 | No | 7.23 | 27 | 82 | 34 | 2.4 | 27.41 | 0.8598
2022-01-10 | 28.17 | 7.15 | 215 | 456 | 428 | 0 | No | 7.28 | 27 | 86 | 40 | 2.1 | 26.83 | 0.8451
2022-01-11 | 29.53 | 7.22 | 220 | 432 | 380 | 0 | No | 7.31 | 23 | 72 | 30 | 2.3 | 27.32 | 0.8859
2022-01-12 | 28.04 | 7.2 | 175 | 396 | 364 | 0 | No | 7.29 | 25 | 78 | 28 | 2.5 | 26.85 | 0.8412
2022-01-13 | 28.79 | 6.98 | 230 | 478 | 432 | 0 | No | 7.23 | 28 | 84 | 37 | 2.2 | 27.53 | 0.8637
2022-01-14 | 28.27 | 7.19 | 210 | 456 | 412 | 0 | No | 7.26 | 26 | 70 | 34 | 2.1 | 27.1 | 0.8481
2022-01-15 | 28.91 | 6.92 | 220 | 462 | 436 | 0 | No | 7.25 | 23 | 74 | 32 | 1.9 | 27.74 | 0.8673
2022-01-16 | 28.66 | 6.97 | 225 | 448 | 416 | 0 | No | 7.36 | 25 | 78 | 29 | 2.3 | 27.49 | 0.8598
2022-01-17 | 28.17 | 7.18 | 235 | 466 | 428 | 0 | No | 7.27 | 28 | 84 | 36 | 2.4 | 26.77 | 0.8451
2022-01-18 | 29.53 | 7.1 | 220 | 440 | 396 | 0 | No | 7.28 | 24 | 72 | 28 | 2 | 27.38 | 0.8859
2022-01-19 | 28.04 | 7.1 | 225 | 458 | 420 | 0 | No | 7.24 | 26 | 76 | 33 | 2.3 | 26.85 | 0.8412
2022-01-20 | 28.4 | 6.9 | 215 | 462 | 432 | 0 | No | 7.24 | 23 | 80 | 38 | 2.2 | 27.17 | 0.852
2022-01-21 | 28.91 | 7.12 | 210 | 454 | 392 | 0 | No | 7.28 | 20 | 72 | 31 | 2.4 | 27.32 | 0.8673
2022-01-22 | 28.66 | 6.88 | 225 | 476 | 448 | 0 | No | 7.25 | 27 | 88 | 37 | 2.1 | 27.52 | 0.8598
2022-01-23 | 29.17 | 6.98 | 220 | 452 | 424 | 0 | No | 7.3 | 26 | 82 | 30 | 2 | 26.93 | 0.8751
2022-01-24 | 28.79 | 7.14 | 240 | 486 | 444 | 0 | No | 7.26 | 23 | 78 | 35 | 2.2 | 27.37 | 0.8637
2022-01-25 | 28.91 | 6.92 | 230 | 458 | 416 | 0 | No | 7.24 | 27 | 86 | 39 | 1.9 | 27.73 | 0.8673
2022-01-26 | 28.66 | 7.1 | 225 | 464 | 420 | 0 | No | 7.32 | 21 | 74 | 32 | 2.3 | 27.37 | 0.8598
2022-01-27 | 28.17 | 7.18 | 215 | 456 | 432 | 0 | No | 7.25 | 24 | 70 | 38 | 2 | 26.07 | 0.8451
2022-01-28 | 28.14 | 7.11 | 235 | 472 | 420 | 0 | No | 7.29 | 26 | 84 | 40 | 2.4 | 26.92 | 0.8442
2022-01-29 | 29.58 | 6.86 | 245 | 496 | 436 | 0 | No | 7.27 | 28 | 88 | 42 | 2.2 | 26.83 | 0.8874
2022-01-30 | 28.53 | 7.2 | 225 | 462 | 412 | 0 | No | 7.25 | 23 | 80 | 35 | 2.1 | 27.37 | 0.8559
2022-01-31 | 28.72 | 6.92 | 220 | 440 | 396 | 0 | No | 7.24 | 25 | 72 | 31 | 2.4 | 27.51 | 0.8616
Total | 889 | [12 empty] | 26.67