## 74 MLD STP Indirapuram LAB
Vehicle
OM & M Cell, Directorate of Urban Bodies, Department of Urban Development, Government of Uttar Pradesh
Uttar Pradesh Jal Nigam, Ghaziabad
VA TECH WABAG LIMITED
MONTHLY LAB REPORT
Name of the plant |  |  |  | STP Indirapuram, Ghaziabad | [5 empty] | Technology |  |  |  | SBR based
Capacity |  |  |  | 74 MLD | [5 empty] | Month |  |  |  | 2021-11-01
Date | Raw Sewage Flow | Raw Sewage Parameters | [5 empty] | Final Outlet Parameters | [5 empty] | Penalty applicability as per Office Memorandum dated: 01/01/2020 Point no :10 | Third Party/UPPCB Report |  | Remark
|  | pH | BOD | COD | TSS | DO | Industrial Effluent (Y/N) | pH | BOD | COD | TSS | DO | sludge generation/Day |  |  | Sludge generation
|  | ---- | mg/L | mg/L | mg/L | mg/L |  | ---- | mg/L | mg/L | mg/L | mg/L
Contract Parameter Mandatory | MLD | 6.5 - 8.0 | 220 - 250 | 400 - 500 | 350 - 500 | 0 |  | 7.0 - 7.5 | <10 | < 100 | < 10 | >6
2021-11-01 | 26.58 | 7.38 | 215 | 426 | 284 | 0 | Yes | 7.42 | 5 | 40 | 4 | 4.6 | 1.0632 |  |  | 1.0632
2021-11-02 | 26.95 | 7.2 | 180 | 354 | 272 | 0 | Yes | 7.26 | 5 | 46 | 5 | 4.8 | 1.078 |  |  | 1.078
2021-11-03 | 25.15 | 6.93 | 190 | 378 | 312 | 0 | Yes | 7.34 | 7 | 58 | 6 | 4.6 | 1.006 |  |  | 1.006
2021-11-04 | 26.36 | 7.22 | 185 | 362 | 330 | 0 | Yes | 7.29 | 5 | 46 | 6 | 4.7 | 1.0544 |  |  | 1.0544
2021-11-05 | 26.63 | 7.34 | 195 | 410 | 344 | 0 | Yes | 7.25 | 6 | 52 | 5 | 4.3 | 1.0652 |  |  | 1.0652
2021-11-06 | 26.72 | 7.18 | 180 | 394 | 328 | 0 | Yes | 7.36 | 5 | 48 | 6 | 5.1 | 1.0688 |  |  | 1.0688
2021-11-07 | 26.75 | 7.25 | 175 | 386 | 320 | 0 | Yes | 7.48 | 4 | 42 | 5 | 5.3 | 1.07 |  |  | 1.07
2021-11-08 | 26.72 | 7.3 | 245 | 524 | 356 | 0 | Yes | 7.42 | 5 | 58 | 7 | 4.2 | 1.0688 |  |  | 1.0688
2021-11-09 | 26.87 | 6.9 | 240 | 492 | 324 | 0 | Yes | 7.24 | 7 | 62 | 6 | 4.8 | 1.0748 |  |  | 1.0748
2021-11-10 | 26.76 | 7.1 | 225 | 458 | 336 | 0 | Yes | 7.25 | 6 | 56 | 5 | 4.6 | 1.0704 |  |  | 1.0704
2021-11-11 | 26.73 | 6.92 | 210 | 436 | 348 | 0 | Yes | 7.43 | 7 | 50 | 7 | 5 | 1.0692 |  |  | 1.0692
2021-11-12 | 26.74 | 6.97 | 235 | 498 | 332 | 0 | Yes | 7.27 | 5 | 44 | 7 | 4.7 | 1.0696 |  |  | 1.0696
2021-11-13 | 26.72 | 7.14 | 240 | 490 | 320 | 0 | Yes | 7.25 | 6 | 52 | 5 | 4.9 | 1.0688 |  |  | 1.0688
2021-11-14 | 26.45 | 7.11 | 230 | 478 | 316 | 0 | Yes | 7.32 | 6 | 56 | 6 | 4.8 | 1.058 |  |  | 1.058
2021-11-15 | 26.94 | 7.21 | 285 | 634 | 312 | 0 | Yes | 7.25 | 8 | 62 | 8 | 4.6 | 1.0776 |  |  | 1.0776
2021-11-16 | 26.68 | 7.15 | 270 | 542 | 344 | 0 | Yes | 7.29 | 6 | 58 | 7 | 4.9 | 1.0672 |  |  | 1.0672
2021-11-17 | 26.77 | 7 | 255 | 516 | 328 | 0 | Yes | 7.22 | 5 | 52 | 5 | 4.7 | 1.0708 |  |  | 1.0708
2021-11-18 | 26.46 | 6.88 | 245 | 492 | 340 | 0 | Yes | 7.12 | 7 | 60 | 7 | 5.1 | 1.0584 |  |  | 1.0584
2021-11-19 | 26.79 | 6.94 | 240 | 510 | 332 | 0 | Yes | 7.28 | 6 | 54 | 6 | 4.5 | 1.0716 |  |  | 1.0716
2021-11-20 | 26.53 | 7.2 | 230 | 472 | 320 | 0 | Yes | 7.27 | 6 | 56 | 6 | 5.2 | 1.0612 |  |  | 1.0612
2021-11-21 | 27.93 | 6.96 | 245 | 496 | 348 | 0 | Yes | 7.25 | 5 | 60 | 8 | 4.8 | 1.1172 |  |  | 1.1172
2021-11-22 | 26.95 | 7.18 | 265 | 544 | 330 | 0 | Yes | 7.32 | 6 | 52 | 7 | 4.7 | 1.078 |  |  | 1.078
2021-11-23 | 26.39 | 7.6 | 255 | 526 | 324 | 0 | Yes | 7.24 | 8 | 58 | 5 | 4.5 | 1.0556 |  |  | 1.0556
2021-11-24 | 26.72 | 7.11 | 260 | 538 | 356 | 0 | Yes | 7.2 | 7 | 62 | 7 | 4.3 | 1.0688 |  |  | 1.0688
2021-11-25 | 26.78 | 7.24 | 195 | 396 | 312 | 0 | Yes | 7.29 | 6 | 44 | 5 | 5.1 | 1.0712 |  |  | 1.0712
2021-11-26 | 26.62 | 7.19 | 185 | 380 | 336 | 0 | Yes | 7.25 | 5 | 48 | 6 | 4.9 | 1.0648 |  |  | 1.0648
2021-11-27 | 26.38 | 7.22 | 270 | 548 | 324 | 0 | Yes | 7.3 | 7 | 56 | 8 | 4.7 | 1.0552 |  |  | 1.0552
2021-11-28 | 26.38 | 7.2 | 265 | 532 | 316 | 0 | Yes | 7.27 | 8 | 60 | 7 | 4.9 | 1.0552 |  |  | 1.0552
2021-11-29 | 26.96 | 7.23 | 270 | 546 | 332 | 0 | Yes | 7.25 | 8 | 58 | 7 | 4.6 | 1.0784 |  |  | 1.0784
2021-11-30 | 26.56 | 6.98 | 275 | 552 | 344 | 0 | Yes | 7.36 | 6 | 48 | 8 | 4.4 | 1.0624 |  |  | 1.0624
Total Flow (MLD) | 799.97 | [11 empty] | 31.9988 |  |  | 31.9988
Name of the plant |  |  |  | STP Indirapuram, Ghaziabad | [5 empty] | Technology |  |  |  | SBR based
Capacity |  |  |  | 74 MLD | [5 empty] | Month |  |  |  | 2021-12-01
Date |  | Raw Sewage Parameters | [5 empty] | Final Outlet Parameters | [5 empty] | Penalty applicability as per Office Memorandum dated: 01/01/2020 Point no :10 | Third Party/UPPCB Report | Remark
| INLET | pH | BOD | COD | TSS | DO | Industrial Effluent (Y/N) | pH | BOD | COD | TSS | DO | Sewage Generation/Day
| MLD | ---- | mg/L | mg/L | mg/L | mg/L |  | ---- | mg/L | mg/L | mg/L | mg/L | MTD
Contract Parameter Mandatory |  | 6.5 - 8.0 | 220 - 250 | 400 - 500 | 350 - 500 | 0 |  | 7.0 - 7.5 | <10 | < 100 | < 10 | >6
2021-12-01 | 28.68 | 7.12 | 265 | 536 | 340 | 0 | Y | 7.24 | 5 | 52 | 6 | 4.8 | 0.8604
2021-12-02 | 28.48 | 6.93 | 250 | 508 | 352 | 0 | Y | 7.27 | 6 | 46 | 8 | 5.1 | 0.8544
2021-12-03 | 28.69 | 7.2 | 260 | 526 | 336 | 0 | Y | 7.24 | 7 | 44 | 9 | 5 | 0.8607
2021-12-04 | 28.28 | 7.24 | 220 | 452 | 304 | 0 | Y | 7.28 | 6 | 40 | 6 | 4.9 | 0.8484
2021-12-05 | 28.63 | 7.22 | 255 | 510 | 328 | 0 | Y | 7.27 | 8 | 58 | 7 | 4.7 | 0.8589
2021-12-06 | 28.49 | 7.15 | 275 | 548 | 364 | 0 | Y | 7.25 | 9 | 54 | 8 | 5.2 | 0.8547
2021-12-07 | 28.73 | 7.23 | 250 | 524 | 356 | 0 | Y | 7.28 | 8 | 48 | 8 | 5 | 0.8619
2021-12-08 | 28.49 | 7.21 | 240 | 486 | 320 | 0 | Y | 7.26 | 7 | 42 | 6 | 5.1 | 0.8547
2021-12-09 | 28.38 | 6.9 | 275 | 554 | 332 | 0 | Y | 7.24 | 7 | 56 | 8 | 4.8 | 0.8514
2021-12-10 | 28.49 | 7.16 | 260 | 532 | 344 | 0 | Y | 7.27 | 8 | 58 | 7 | 4.6 | 0.8547
2021-12-11 | 28.71 | 7.12 | 285 | 578 | 492 | 0 | Y | 7.25 | 7 | 60 | 9 | 4.9 | 0.8613
2021-12-12 | 28.41 | 7.2 | 280 | 564 | 476 | 0 | Y | 7.28 | 8 | 54 | 8 | 5.1 | 0.8523
2021-12-13 | 28.61 | 7.14 | 310 | 628 | 512 | 0 | Y | 7.3 | 6 | 48 | 8 | 4.8 | 0.8583
2021-12-14 | 28.64 | 7.17 | 325 | 640 | 524 | 0 | Y | 7.23 | 7 | 56 | 9 | 4.7 | 0.8592
2021-12-15 | 28.49 | 7.13 | 305 | 612 | 488 | 0 | Y | 7.27 | 5 | 50 | 7 | 5.3 | 0.8547
2021-12-16 | 28.39 | 7.21 | 245 | 506 | 460 | 0 | Y | 7.33 | 8 | 58 | 6 | 4.9 | 0.8517
2021-12-17 | 28.19 | 7.2 | 270 | 552 | 472 | 0 | Y | 7.26 | 6 | 52 | 8 | 4.8 | 0.8457
2021-12-18 | 28.47 | 7.18 | 240 | 490 | 448 | 0 | Y | 7.24 | 6 | 48 | 7 | 4.8 | 0.8541
2021-12-19 | 28.75 | 7.15 | 230 | 478 | 412 | 0 | Y | 7.27 | 8 | 56 | 6 | 5.1 | 0.8625
2021-12-20 | 28.38 | 7.17 | 255 | 516 | 436 | 0 | Y | 7.24 | 8 | 60 | 9 | 5.2 | 0.8514
2021-12-21 | 28.4 | 7.14 | 290 | 584 | 444 | 0 | Y | 7.35 | 7 | 62 | 8 | 5 | 0.852
2021-12-22 | 28.63 | 7.12 | 270 | 566 | 428 | 0 | Y | 7.27 | 8 | 54 | 6 | 4.8 | 0.8589
2021-12-23 | 28.69 | 7.19 | 255 | 538 | 396 | 0 | Y | 7.38 | 8 | 56 | 6 | 5.1 | 0.8607
2021-12-24 | 28.47 | 7.15 | 250 | 512 | 410 | 0 | Y | 7.34 | 7 | 48 | 8 | 4.7 | 0.8541
2021-12-25 | 28.49 | 7.2 | 225 | 468 | 372 | 0 | Y | 7.26 | 6 | 42 | 6 | 4.6 | 0.8547
2021-12-26 | 28.52 | 7.16 | 240 | 482 | 416 | 0 | Y | 7.29 | 9 | 56 | 7 | 4.4 | 0.8556
2021-12-27 | 28.488 | 7.13 | 265 | 522 | 432 | 0 | Y | 7.36 | 8 | 64 | 9 | 4.2 | 0.85464
2021-12-28 | 28.61 | 7.18 | 260 | 518 | 424 | 0 | Y | 7.28 | 9 | 58 | 8 | 4.5 | 0.8583
2021-12-29 | 28.81 | 7.22 | 245 | 496 | 376 | 0 | Y | 7.25 | 7 | 46 | 6 | 4.1 | 0.8643
2021-12-30 | 28.59 | 7.19 | 250 | 510 | 396 | 0 | Y | 7.27 | 8 | 52 | 7 | 4.3 | 0.8577
2021-12-31 | 28.53 | 7.21 | 260 | 538 | 380 | 0 | Y | 7.22 | 9 | 60 | 8 | 4.1 | 0.8559
Total Flow (MLD) | 886.61 | [11 empty] | 26.5382
OM & M Cell, Directorate of Urban Bodies, Department of Urban Development, Government of Uttar Pradesh
Uttar Pradesh Jal Nigam, Ghaziabad
VA TECH WABAG LIMITED
MONTHLY LAB REPORT
Name of the plant |  |  |  | STP Indirapuram, Ghaziabad | [5 empty] | Technology
Capacity |  |  |  | 74 MLD | [5 empty] | Month
Date | Raw Sewage Flow | Raw Sewage Parameters | [5 empty] | Final Outlet Parameters | [5 empty] | Remark
|  | pH | BOD | COD | TSS | DO | Industrial Effluent (Y/N) | pH | BOD | COD | TSS | DO | Sludge Generation/Day
|  | ---- | mg/L | mg/L | mg/L | mg/L |  | ---- | mg/L | mg/L | mg/L | mg/L | MTM
Contract Parameter Mandatory | MLD | 6.5 - 8.0 | 220 - 250 | 400 - 500 | 350 - 500 | 0 |  | 7.0 - 7.5 | <10 | < 100 | < 10 | >6
2022-01-01 | 28.63 | 7.2 | 315 | 610 | 460 | 0 | Y | 7.25 | 7 | 62 | 8 | 4.4 | 0.8589
2022-01-02 | 28.73 | 7.17 | 290 | 584 | 436 | 0 | Y | 7.27 | 8 | 58 | 6 | 3.9 | 0.8619
2022-01-03 | 28.42 | 7.19 | 305 | 596 | 448 | 0 | Y | 7.23 | 6 | 54 | 9 | 4.1 | 0.8526
2022-01-04 | 28.85 | 7.16 | 320 | 624 | 424 | 0 | Y | 7.36 | 7 | 66 | 7 | 4.3 | 0.8655
2022-01-05 | 28.62 | 7.22 | 275 | 570 | 432 | 0 | Y | 7.24 | 9 | 62 | 8 | 3.8 | 0.8586
2022-01-06 | 28.5 | 7.2 | 265 | 542 | 396 | 0 | Y | 7.35 | 7 | 56 | 7 | 4.2 | 0.855
2022-01-07 | 28.25 | 7.21 | 395 | 786 | 472 | 0 | Y | 7.33 | 7 | 64 | 9 | 4.5 | 0.8475
2022-01-08 | 28.15 | 7.18 | 285 | 568 | 428 | 0 | Y | 7.29 | 9 | 58 | 8 | 4.1 | 0.8445
2022-01-09 | 28.92 | 7.15 | 260 | 532 | 410 | 0 | Y | 7.31 | 8 | 52 | 6 | 4 | 0.8676
2022-01-10 | 28.1 | 7.23 | 405 | 782 | 624 | 0 | Y | 7.42 | 6 | 66 | 9 | 4.2 | 0.843
2022-01-11 | 28.33 | 7.17 | 325 | 638 | 488 | 0 | Y | 7.36 | 7 | 60 | 8 | 4.4 | 0.8499
2022-01-12 | 28.15 | 7.24 | 290 | 578 | 452 | 0 | Y | 7.4 | 8 | 54 | 7 | 4.3 | 0.8445
2022-01-13 | 28.77 | 7.29 | 275 | 562 | 416 | 0 | Y | 7.38 | 7 | 48 | 8 | 3.8 | 0.8631
2022-01-14 | 28.67 | 7.2 | 315 | 646 | 468 | 0 | Y | 7.33 | 9 | 68 | 9 | 4.1 | 0.8601
2022-01-15 | 28.45 | 7.22 | 255 | 538 | 392 | 0 | Y | 7.31 | 7 | 56 | 6 | 4.2 | 0.8535
2022-01-16 | 28.72 | 7.19 | 360 | 732 | 524 | 0 | Y | 7.42 | 8 | 66 | 9 | 4 | 0.8616
2022-01-17 | 28.25 | 7.23 | 295 | 610 | 476 | 0 | Y | 7.36 | 6 | 54 | 7 | 4.3 | 0.8475
2022-01-18 | 28.45 | 7.25 | 340 | 694 | 492 | 0 | Y | 7.34 | 9 | 58 | 8 | 3.9 | 0.8535
2022-01-19 | 28.07 | 7.19 | 280 | 570 | 408 | 0 | Y | 7.38 | 8 | 52 | 6 | 4.4 | 0.8421
2022-01-20 | 28.15 | 7.22 | 265 | 536 | 396 | 0 | Y | 7.29 | 7 | 44 | 8 | 4.2 | 0.8445
2022-01-21 | 28.07 | 7.2 | 270 | 522 | 380 | 0 | Y | 7.42 | 8 | 46 | 7 | 4.5 | 0.8421
2022-01-22 | 28.86 | 7.17 | 235 | 486 | 412 | 0 | Y | 7.33 | 6 | 42 | 7 | 4.3 | 0.8658
2022-01-23 | 28.1 | 7.19 | 275 | 552 | 436 | 0 | Y | 7.37 | 7 | 56 | 8 | 4.1 | 0.843
2022-01-24 | 28.07 | 7.24 | 335 | 680 | 448 | 0 | Y | 7.32 | 8 | 62 | 9 | 4.4 | 0.8421
2022-01-25 | 28.02 | 7.18 | 350 | 692 | 432 | 0 | Y | 7.27 | 7 | 58 | 8 | 4.2 | 0.8406
2022-01-26 | 28.63 | 7.2 | 330 | 668 | 392 | 0 | Y | 7.29 | 9 | 46 | 9 | 4.3 | 0.8589
2022-01-27 | 28.02 | 7.23 | 350 | 702 | 416 | 0 | Y | 7.34 | 6 | 64 | 9 | 4.5 | 0.8406
2022-01-28 | 28.75 | 7.25 | 305 | 624 | 428 | 0 | Y | 7.37 | 6 | 48 | 6 | 4.2 | 0.8625
2022-01-29 | 28.55 | 7.22 | 285 | 588 | 410 | 0 | Y | 7.31 | 7 | 52 | 8 | 4.7 | 0.8565
2022-01-30 | 28.25 | 7.19 | 315 | 640 | 464 | 0 | Y | 7.28 | 8 | 66 | 7 | 4 | 0.8475
2022-01-31 | 28.82 | 7.23 | 310 | 614 | 408 | 0 | Y | 7.3 | 6 | 48 | 8 | 4.4 | 0.8646
Total | 881.32 | [11 empty] | 26.4396
VA Tech Wabag | [9 empty] | UP Jal Nigam Ghaziabad
63.9976