## Bapudham 56
GHAZIABAD DOVELOPMENT AUTHORITY
SITE :- 56 MLD SEWAGE TREATMENT PLANT
LOCATION :- MADHUBAN BAPUDHAM, GHAZIABAD
AGENCY :- M/S VIBHOR VAIBHAV INFRA (P) LTD.
OPERATION & MAINTANANCE 25-09-2019 TO 25-09-2024
MONTH AND YEAR :-Nov- 2021
SUMMARY OF REPORTS FORMAT FOR DAILY TESTING
DATE |  |  | INLET PARAMETERS |  |  |  | OUTLET PARAMETER |  |  |  | Sludge Generation/Day
| INLET | OUTLET | PH | TSS | COD | BOD | PH | TSS | COD | BOD
| MLD | MLD |  | mg/l | mg/l | mg/l |  | mg/l | mg/l | mg/l
2021-11-01 | 25.9 | 24.56 | 6.81 | 195 | 210 | 114 | 7.01 | 9.3 | 82 | 9.4 | 1.027
2021-11-02 | 25.64 | 24.85 | 6.72 | 198 | 203 | 116.5 | 7.01 | 9.2 | 73 | 9.8 | 1.052
2021-11-03 | 25.42 | 24.21 | 6.65 | 202 | 216 | 115.5 | 7.08 | 9.7 | 66 | 9.6 | 1.027
2021-11-04 | 25.53 | 24.97 | 6.8 | 209 | 224 | 114.5 | 7.04 | 9.6 | 64 | 9.3 | 1.027
2021-11-05 | 25.34 | 24.89 | 6.78 | 188 | 208 | 117.5 | 7.02 | 9.8 | 78 | 9.9 | 0.901
2021-11-06 | 25.73 | 24.03 | 6.87 | 180 | 213 | 121 | 7.1 | 9.4 | 81 | 10.2 | 1.052
2021-11-07 | 25.76 | 24.2 | 6.89 | 192 | 208 | 116.5 | 7.11 | 10.2 | 74 | 9.2 | 1.072
2021-11-08 | 25.95 | 24.86 | 6.86 | 186 | 215 | 112.5 | 7.06 | 10.4 | 78 | 9 | 1.062
2021-11-09 | 25.56 | 24.18 | 6.91 | 171 | 221 | 111.5 | 7.14 | 9.8 | 63 | 9.4 | 1.042
2021-11-10 | 25.35 | 24.17 | 6.9 | 191 | 212 | 113.5 | 7.17 | 9.7 | 58 | 9.6 | 0.928
2021-11-11 | 25.5 | 24.86 | 6.89 | 188 | 224 | 118.5 | 7.1 | 9.8 | 61 | 9.8 | 1.028
2021-11-12 | 25.35 | 24.78 | 6.77 | 177 | 208 | 112.5 | 7.13 | 10.2 | 68 | 9.8 | 1.082
2021-11-13 | 25.22 | 24.02 | 6.91 | 190 | 220 | 111.5 | 7.39 | 10.4 | 81 | 10.2 | 0.962
2021-11-14 | 25.37 | 24.26 | 6.84 | 182 | 214 | 111.5 | 7.2 | 9.6 | 78 | 9.8 | 1.021
2021-11-15 | 25.58 | 23.95 | 6.66 | 169 | 211 | 113.5 | 7.21 | 9.9 | 87 | 9.8 | 0.941
2021-11-16 | 25.34 | 24.08 | 6.75 | 170 | 220 | 108.5 | 7.14 | 10.6 | 79 | 9.4 | 1.021
2021-11-17 | 25.45 | 23.94 | 6.84 | 175 | 215 | 115 | 7.28 | 10.5 | 84 | 10.1 | 0.971
2021-11-18 | 25.63 | 24.13 | 6.7 | 191 | 206 | 115.6 | 7.13 | 10.3 | 76 | 10.5 | 1.026
2021-11-19 | 25.38 | 24.46 | 6.89 | 184 | 217 | 112.7 | 7.17 | 10.2 | 86 | 10.4 | 1.025
2021-11-20 | 25.59 | 24.73 | 7.07 | 167 | 206 | 118.5 | 7.26 | 10.1 | 74 | 10.2 | 0.951
2021-11-21 | 25.32 | 24.48 | 9.58 | 174 | 205 | 125 | 7.24 | 10.6 | 73 | 9.6 | 1.052
2021-11-22 | 25.91 | 24.47 | 6.78 | 194 | 192 | 115.5 | 7.21 | 11.2 | 67 | 9.4 | 0.971
2021-11-23 | 25.46 | 24.93 | 7.08 | 179 | 185 | 118.5 | 7.22 | 10 | 73 | 9.2 | 1.025
2021-11-24 | 25.47 | 24.77 | 6.94 | 167 | 190 | 116.5 | 7.26 | 9.2 | 80 | 9.1 | 0.961
2021-11-26 | 25.48 | 24.17 | 6.85 | 171 | 198 | 119 | 7.22 | 9.4 | 72 | 9.5 | 1.027
2021-11-26 | 25.46 | 24.03 | 6.8 | 180 | 189 | 118.5 | 7.16 | 9.8 | 66 | 9.8 | 1.024
2021-11-27 | 25.3 | 24.62 | 6.86 | 186 | 192 | 116 | 7.21 | 9.7 | 70 | 10.1 | 1.058
2021-11-28 | 25.41 | 23.82 | 6.87 | 173 | 203 | 111.5 | 7.22 | 10.2 | 77 | 9.3 | 1.072
2021-11-29 | 25.94 | 24.56 | 6.87 | 185 | 206 | 113.5 | 7.24 | 9.8 | 83 | 9.7 | 1.062
2021-11-30 | 25.67 | 24.48 | 7.02 | 184 | 193 | 115.5 | 7.2 | 10.1 | 74 | 10.3 | 1.043
Total | 766.01 | 732.46 | [8 empty] | 30.513
DATE |  |  | INLET PARAMETERS PH: INLET PARAMETERS; OUTLET PARAMETER PH: OUTLET PARAMETER | Total Sludge Generation/Day
|  |  | PH | TSS | COD | BOD | PH | TSS | COD | BOD
|  |  |  | mg/l | mg/l | mg/l |  | mg/l | mg/l | mg/l
2021-12-01 | 28.9 | 27.56 | 6.92 | 182 | 174 | 107.5 | 7.04 | 9.7 | 69 | 9.4 | 0.872
2021-12-02 | 28.64 | 27.85 | 6.81 | 191 | 168 | 104.5 | 7.01 | 9.5 | 72 | 9.7 | 0.823
2021-12-03 | 28.42 | 27.21 | 6.94 | 188 | 180 | 102.5 | 7.08 | 10.5 | 64 | 10.1 | 0.851
2021-12-04 | 28.53 | 27.97 | 7.03 | 202 | 193 | 101.5 | 7.16 | 9 | 59 | 9.6 | 0.862
2021-12-05 | 28.34 | 27.89 | 6.88 | 176 | 209 | 103.5 | 7.05 | 10.2 | 70 | 9.9 | 0.89
2021-12-06 | 28.73 | 27.03 | 7.055 | 180 | 188 | 105 | 7.21 | 9.9 | 55 | 9.5 | 0.826
2021-12-07 | 28.76 | 27.2 | 6.79 | 194 | 205 | 108.5 | 6.94 | 10.3 | 67 | 9.8 | 0.895
2021-12-08 | 27.95 | 26.34 | 6.81 | 206 | 195 | 110 | 6.98 | 10.9 | 60 | 10.1 | 0.863
2021-12-09 | 27.56 | 27.18 | 7.02 | 212 | 179 | 107.5 | 7.23 | 9.8 | 72 | 9.7 | 0.827
2021-12-10 | 27.35 | 27.17 | 6.92 | 201 | 175 | 109.5 | 7.16 | 8.9 | 68 | 9.8 | 0.818
2021-12-11 | 28.5 | 27.86 | 6.84 | 194 | 163 | 111.5 | 7.12 | 8.6 | 60 | 10.1 | 0.856
2021-12-12 | 27.35 | 27.78 | 6.9 | 199 | 170 | 110 | 7.17 | 8.8 | 59 | 9.9 | 0.895
2021-12-13 | 27.22 | 27.02 | 6.98 | 212 | 168 | 112.5 | 7.22 | 9.3 | 64 | 9.6 | 0.887
2021-12-14 | 28.37 | 27.26 | 7.05 | 195 | 174 | 114.5 | 7.29 | 9 | 69 | 9.8 | 0.852
2021-12-15 | 27.58 | 27.95 | 7.01 | 186 | 165 | 115 | 7.24 | 8.7 | 72 | 9.9 | 0.818
2021-12-16 | 27.34 | 27.08 | 6.9 | 192 | 172 | 117.5 | 7.18 | 9.2 | 55 | 10.3 | 0.836
2021-12-17 | 28.45 | 27.54 | 6.82 | 188 | 169 | 116.5 | 7.15 | 8.5 | 50 | 9.7 | 0.827
2021-12-18 | 28.63 | 27.13 | 6.74 | 192 | 177 | 113.5 | 7.09 | 9.4 | 61 | 9.5 | 0.897
2021-12-19 | 27.38 | 26.46 | 6.7 | 201 | 184 | 115 | 7.06 | 9.8 | 68 | 9.8 | 0.859
2021-12-20 | 27.59 | 26.73 | 6.81 | 196 | 189 | 118.5 | 7.01 | 9.6 | 57 | 9.4 | 0.826
2021-12-21 | 28.32 | 27.48 | 6.76 | 185 | 193 | 120 | 7.07 | 9.3 | 51 | 9.9 | 0.842
2021-12-22 | 28.91 | 27.47 | 6.84 | 190 | 186 | 117.5 | 7.04 | 9.5 | 49 | 9.7 | 0.821
2021-12-23 | 28.46 | 27.93 | 6.8 | 187 | 192 | 119.5 | 7.14 | 9.4 | 57 | 10.1 | 0.868
2021-12-24 | 28.47 | 27.77 | 6.92 | 180 | 196 | 121.5 | 7.11 | 9 | 64 | 10.3 | 0.815
2021-12-25 | 28.47 | 27.17 | 6.9 | 192 | 204 | 118.5 | 7.19 | 9.6 | 77 | 9.8 | 0.826
2021-12-26 | 28.46 | 27.03 | 6.83 | 181 | 198 | 115 | 7.12 | 9.1 | 81 | 9.5 | 0.828
2021-12-27 | 28.3 | 27.62 | 6.97 | 197 | 207 | 113.5 | 7.18 | 9.7 | 72 | 9.3 | 0.863
2021-12-28 | 28.41 | 27.32 | 6.92 | 175 | 194 | 112.5 | 7.16 | 9.2 | 68 | 9.1 | 0.849
2021-12-29 | 28.94 | 27.56 | 6.81 | 182 | 198 | 10 | 7.19 | 9.8 | 62 | 8.8 | 0.864
2021-12-30 | 28.67 | 27.48 | 6.9 | 179 | 191 | 108.5 | 7.25 | 9 | 58 | 8.5 | 0.879
2021-12-31 | 28.54 | 27.73 | 6.85 | 184 | 203 | 105 | 7.17 | 9.3 | 65 | 8.2 | 0.828
| 875.54 |  | OUTLET PARAMETER PH: SITE INCHARGE | 26.363
DATE |  |  | INLET PARAMETERS PH: INLET PARAMETERS; OUTLET PARAMETER PH: OUTLET PARAMETER | Desludging/Day
| INLET | OUTLET | PH | TSS | COD | BOD | PH | TSS | COD | BOD
|  |  |  | mg/l | mg/l | mg/l |  | mg/l | mg/l | mg/l
2022-01-01 | 28.27 | 27.25 | 6.86 | 189 | 223 | 110 | 7.12 | 9.3 | 59 | 9.6 | 0.857
2022-01-02 | 27.38 | 26.83 | 6.95 | 174 | 254 | 107.5 | 7.19 | 8.8 | 64 | 9.4 | 0.863
2022-01-03 | 27.64 | 26.27 | 6.82 | 169 | 239 | 105 | 7.16 | 8.4 | 52 | 9.1 | 0.819
2022-01-04 | 28.75 | 26.65 | 6.98 | 181 | 220 | 108.5 | 7.21 | 8.9 | 48 | 9.5 | 0.873
2022-01-05 | 28.43 | 27.63 | 6.71 | 193 | 211 | 111.5 | 7.06 | 9.5 | 44 | 9.8 | 0.873
2022-01-06 | 27.78 | 26.38 | 6.85 | 188 | 228 | 115 | 7.09 | 8.8 | 51 | 10.2 | 0.89
2022-01-07 | 27.99 | 26.2 | 6.9 | 172 | 236 | 112.5 | 7.14 | 8.6 | 58 | 9.9 | 0.837
2022-01-08 | 28.22 | 27.43 | 6.74 | 196 | 241 | 109.5 | 7.17 | 9.4 | 62 | 9.6 | 0.827
2022-01-09 | 28.51 | 27.37 | 6.88 | 202 | 238 | 105 | 7.23 | 9.7 | 55 | 9.3 | 0.835
2022-01-10 | 28.26 | 27.68 | 6.94 | 185 | 226 | 110 | 7.28 | 9.3 | 60 | 9.8 | 0.836
2022-01-11 | 28.57 | 27.64 | 6.81 | 172 | 240 | 112.5 | 7.19 | 9 | 67 | 10.1 | 0.8364
2022-01-12 | 28.37 | 27.48 | 6.89 | 164 | 235 | 108.5 | 7.23 | 9.8 | 74 | 9.7 | 0.836
2022-01-13 | 28.26 | 27.31 | 6.92 | 191 | 221 | 113.5 | 7.29 | 10.4 | 81 | 10.2 | 0.837
2022-01-14 | 28.62 | 27.35 | 6.84 | 182 | 214 | 111.5 | 7.2 | 9.6 | 77 | 9.9 | 0.831
2022-01-15 | 28.42 | 27.48 | 6.53 | 177 | 208 | 115 | 7.11 | 10.5 | 85 | 10.4 | 0.892
2022-01-16 | 28.14 | 27.16 | 6.73 | 163 | 217 | 112.5 | 7.16 | 10.9 | 72 | 10.2 | 0.836
2022-01-17 | 28.67 | 27.64 | 6.89 | 180 | 209 | 110 | 7.25 | 10.3 | 81 | 10 | 0.872
2022-01-18 | 28.24 | 27.23 | 6.8 | 189 | 202 | 113.5 | 7.25 | 11.2 | 75 | 10.4 | 0.859
2022-01-19 | 28.36 | 27.25 | 6.88 | 182 | 217 | 115 | 7.17 | 10.7 | 89 | 10.5 | 0.826
2022-01-20 | 28.35 | 27.43 | 7.01 | 174 | 210 | 118.5 | 7.21 | 10.2 | 77 | 10.2 | 0.836
2022-01-21 | 28.92 | 27.88 | 6.89 | 183 | 203 | 120 | 7.24 | 10.8 | 70 | 9.9 | 0.827
2022-01-22 | 27.68 | 27.57 | 6.94 | 193 | 198 | 117.5 | 7.2 | 11.3 | 68 | 9.5 | 0.863
2022-01-23 | 28.46 | 27.23 | 7.02 | 180 | 187 | 116.5 | 7.22 | 10.1 | 74 | 9.3 | 0.816
2022-01-24 | 28.42 | 27.57 | 6.98 | 169 | 191 | 118.5 | 7.25 | 9.3 | 81 | 9 | 0.873
2022-01-25 | 28.71 | 27.73 | 6.87 | 173 | 200 | 120 | 7.23 | 9.5 | 73 | 9.6 | 0.839
2022-01-26 | 28.53 | 27.63 | 6.95 | 181 | 189 | 117.5 | 7.19 | 9.9 | 67 | 9.9 | 0.894
2022-01-27 | 28.74 | 27.22 | 6.82 | 189 | 194 | 115 | 7.21 | 9.8 | 71 | 10.2 | 0.895
2022-01-28 | 29.1 | 2822 | 6.93 | 174 | 205 | 112.5 | 7.24 | 10.3 | 78 | 9.4 | 0.898
2022-01-29 | 28.73 | 27.36 | 6.98 | 193 | 207 | 116.5 | 7.27 | 9.9 | 82 | 9.8 | 0.858
2022-01-30 | 28.58 | 27.34 | 7.01 | 186 | 196 | 118.5 | 7.29 | 10.2 | 75 | 104 | 0.837
2022-01-31 | 28.46 | 27.33 | 7.04 | 194 | 212 | 121.5 | 7.26 | 10.5 | 84 | 9.7 | 0.858
Total | 879.56 | [9 empty] | 26.4294