## Dhundahera 76 MLD
STATE GANGA RIVER CONSERVATION AGENCY (DEPARTMENT OF URBAN DEVELOPMENT, UTTAR PRADESH)
Long-term Operation, Maintenance and Management of the Sewage Treatment System and Sewer network in the State of Uttar Pradesh {Package-8, Zone-Ghaziabad (UP)}
VA TECH WABAG LIMITED
LABORATORY LOG SHEETS-I
Name of the plant |  |  |  |  | STP Plant Dundahera
Capacity |  |  |  |  | 76 MLD
Technology |  |  |  |  | SBR Based Technology
Month |  |  |  |  | 2021-11-01
Date |  |  | Raw Sewage |  |  |  |  | Final Outlet | [5 empty] | Remarks
| Inlet flow | Outlet Flow | pH | BOD | COD | TSS | DO | pH | BOD | COD | TSS | DO | Sludge Generation/Day
| MLD | MLD | ---- | mg/L | mg/L | mg/L | ppm | ---- | mg/L | mg/L | mg/L | ppm | MTM
2021-11-01 | 25.77 | 24.74 | 7 | 195 | 374 | 346 | 0.2 | 6.9 | 21 | 55 | 33 | 2.3 | 1.0308
2021-11-02 | 25.78 | 24.61 | 7.2 | 190 | 382 | 360 | 0.4 | 7.1 | 17 | 42 | 21 | 2.1 | 1.0312
2021-11-03 | 25.54 | 24.42 | 7.4 | 200 | 394 | 353 | 0.2 | 7.2 | 25 | 60 | 30 | 2.3 | 1.0216
2021-11-04 | 25.65 | 24.59 | 7.2 | 195 | 400 | 366 | 0.3 | 7.1 | 19 | 39 | 41 | 2.3 | 1.026
2021-11-05 | 25.73 | 24.69 | 7.3 | 190 | 388 | 350 | 0.4 | 7.2 | 23 | 52 | 33 | 2.1 | 1.0292
2021-11-06 | 25.58 | 24.44 | 7.3 | 200 | 394 | 375 | 0.4 | 7 | 17 | 48 | 40 | 2.3 | 1.0232
2021-11-07 | 25.79 | 24.63 | 7.1 | 185 | 381 | 359 | 0.3 | 6.9 | 27 | 41 | 29 | 2.2 | 1.0316
2021-11-08 | 25.52 | 24.33 | 7.2 | 190 | 402 | 376 | 0.4 | 7.1 | 18 | 58 | 34 | 2.2 | 1.0208
2021-11-09 | 25.94 | 24.88 | 6.9 | 200 | 371 | 350 | 0.3 | 6.8 | 21 | 44 | 22 | 2 | 1.0376
2021-11-10 | 25.49 | 24.35 | 7.3 | 195 | 384 | 370 | 0.2 | 7.2 | 17 | 61 | 36 | 2.1 | 1.0196
2021-11-11 | 25.67 | 24.58 | 7.2 | 190 | 370 | 345 | 0.4 | 7.1 | 24 | 42 | 23 | 2.2 | 1.0268
2021-11-12 | 25.49 | 24.49 | 7.4 | 200 | 410 | 376 | 0.3 | 7.2 | 27 | 65 | 40 | 2.3 | 1.0196
2021-11-13 | 25.53 | 24.59 | 7.3 | 185 | 382 | 360 | 0.2 | 7.2 | 20 | 40 | 29 | 2.1 | 1.0212
2021-11-14 | 25.45 | 24.33 | 7.4 | 190 | 396 | 378 | 0.4 | 7.3 | 23 | 58 | 41 | 2.2 | 1.018
2021-11-15 | 25.61 | 24.59 | 7.2 | 200 | 374 | 346 | 0.3 | 7.1 | 21 | 48 | 21 | 2.1 | 1.0244
2021-11-16 | 25.5 | 24.4 | 7.3 | 195 | 400 | 366 | 0.2 | 7.2 | 27 | 60 | 32 | 2.3 | 1.02
2021-11-17 | 25.66 | 24.52 | 7 | 195 | 381 | 348 | 0.4 | 6.9 | 20 | 48 | 40 | 2.3 | 0.94942
2021-11-18 | 25.62 | 24.41 | 7.3 | 180 | 390 | 370 | 0.3 | 7.2 | 17 | 57 | 29 | 2.2 | 1.0248
2021-11-19 | 25.73 | 24.63 | 7.2 | 195 | 372 | 346 | 0.2 | 7.1 | 22 | 42 | 38 | 2.1 | 1.0292
2021-11-20 | 25.54 | 24.37 | 7.1 | 190 | 392 | 365 | 0.4 | 7 | 18 | 49 | 30 | 2.3 | 1.0216
2021-11-21 | 25.63 | 24.55 | 7.3 | 200 | 402 | 378 | 0.4 | 7.2 | 26 | 64 | 44 | 2.2 | 1.0252
2021-11-22 | 25.56 | 24.45 | 7.2 | 190 | 384 | 348 | 0.2 | 7.1 | 19 | 50 | 32 | 2.1 | 1.0224
2021-11-23 | 25.75 | 24.61 | 7.3 | 195 | 392 | 373 | 0.3 | 7.2 | 27 | 66 | 28 | 2.3 | 1.03
2021-11-24 | 25.35 | 24.28 | 7.2 | 180 | 410 | 388 | 0.4 | 7.1 | 20 | 74 | 42 | 2 | 1.014
2021-11-25 | 25.5 | 24.38 | 7.3 | 195 | 388 | 360 | 0.3 | 7.2 | 16 | 60 | 30 | 2.1 | 1.02
2021-11-26 | 25.65 | 24.53 | 7.2 | 190 | 372 | 342 | 0.2 | 7.1 | 21 | 82 | 37 | 2.2 | 1.026
2021-11-27 | 25.42 | 24.27 | 7.3 | 200 | 396 | 366 | 0.2 | 7.2 | 26 | 46 | 30 | 2 | 1.0168
2021-11-28 | 25.47 | 24.38 | 7.3 | 195 | 382 | 368 | 0.4 | 7.2 | 20 | 72 | 42 | 2.3 | 0.96786
2021-11-29 | 25.38 | 24.25 | 7.2 | 190 | 392 | 374 | 0.3 | 7.1 | 17 | 46 | 37 | 2.1 | 0.96444
2021-11-30 | 25.74 | 24.61 | 7.4 | 185 | 387 | 356 | 0.2 | 7.3 | 19 | 60 | 48 | 2.2 | 1.0296
| 768.04 | [11 empty] | 30.5429
STATE GANGA RIVER CONSERVATION AGENCY (DEPARTMENT OF URBAN DEVELOPMENT, UTTAR PRADESH)
Long-term Operation, Maintenance and Management of the Sewage Treatment System and Sewer network in the State of Uttar Pradesh {Package-8, Zone-Ghaziabad (UP)}
VA TECH WABAG LIMITED
LABORATORY LOG SHEETS-I
Name of the plant |  |  | Raw Sewage BOD: STP Plant Dundahera
Capacity |  |  | Raw Sewage BOD: 76 MLD
Technology |  |  | Raw Sewage BOD: SBR Based Technology
Month |  |  | Raw Sewage BOD: 2021-12-01
Date | Flow | Raw Sewage
Date | Flow | pH | BOD | COD | TSS | DO | BOD | COD | TSS | DO | Out flow | Desludgin/Day | Remarks
|  | ---- | mg/L | mg/L | mg/L | ppm | mg/L | mg/L | mg/L | ppm | MLD | MTM
2021-12-01 | 28.9 | 7.2 | 195 | 382 | 360 | 0.3 | 21 | 62 | 36 | 4.1 | 27.43 | 0.8959
2021-12-02 | 28.64 | 7.1 | 185 | 374 | 347 | 0.4 | 16 | 54 | 30 | 4.2 | 27.39 | 0.88784
2021-12-03 | 28.42 | 7.3 | 200 | 392 | 370 | 0.2 | 27 | 62 | 41 | 4.3 | 27.58 | 0.88102
2021-12-04 | 28.53 | 7.2 | 190 | 380 | 356 | 0.3 | 20 | 50 | 33 | 4 | 27.64 | 0.88443
2021-12-05 | 28.34 | 7.3 | 185 | 402 | 378 | 0.4 | 23 | 68 | 43 | 4.2 | 27.45 | 0.87854
2021-12-06 | 28.73 | 7.2 | 200 | 382 | 360 | 0.2 | 18 | 52 | 38 | 4.1 | 27.57 | 0.89063
2021-12-07 | 28.76 | 7.1 | 190 | 374 | 348 | 0.3 | 28 | 44 | 40 | 4 | 27.58. | 0.89156
2021-12-08 | 27.95 | 7.3 | 185 | 391 | 367 | 0.2 | 17 | 60 | 31 | 44.2 | 26.93 | 0.86645
2021-12-09 | 27.56 | 7.3 | 200 | 370 | 341 | 0.4 | 21 | 43 | 27 | 4.3 | 26.77 | 0.85436
2021-12-10 | 27.35 | 7.1 | 190 | 387 | 358 | 0.3 | 16 | 70 | 42 | 4.1 | 26.57 | 0.84785
2021-12-11 | 28.5 | 7.3 | 185 | 400 | 350 | 0.2 | 23 | 48 | 30 | 4.3 | 27.46 | 0.8835
2021-12-12 | 27.35 | 7.2 | 200 | 408 | 386 | 0.4 | 28 | 84 | 47 | 4.1 | 26.3 | 0.84785
2021-12-13 | 27.22 | 7.4 | 180 | 391 | 364 | 0.3 | 18 | 53 | 38 | 4.2 | 26.32 | 0.84382
2021-12-14 | 28.37 | 7.3 | 205 | 362 | 343 | 0.4 | 26 | 45 | 30 | 4.2 | 27.72 | 0.87947
2021-12-15 | 27.58 | 7.2 | 190 | 377 | 356 | 0.2 | 20 | 62 | 41 | 4 | 26.41 | 0.85498
2021-12-16 | 27.34 | 7.3 | 195 | 392 | 372 | 0.4 | 15 | 47 | 33 | 4.3 | 26.73 | 0.84754
2021-12-17 | 28.45 | 7.1 | 190 | 364 | 347 | 0.3 | 19 | 58 | 29 | 4.1 | 27.38 | 0.88195
2021-12-18 | 28.63 | 7.2 | 185 | 380 | 359 | 0.4 | 23 | 49 | 40 | 4.2 | 27.61 | 0.88753
2021-12-19 | 27.38 | 7.3 | 190 | 410 | 377 | 0.2 | 27 | 86 | 45 | 4 | 26.45 | 0.84878
2021-12-20 | 27.59 | 7.2 | 200 | 376 | 352 | 0.3 | 19 | 62 | 39 | 4.2 | 26.41 | 0.85529
2021-12-21 | 28.32 | 7.1 | 195 | 382 | 364 | 0.4 | 16 | 57 | 41 | 4.1 | 27.26 | 0.87792
2021-12-22 | 28.91 | 7.3 | 180 | 371 | 346 | 0.2 | 21 | 60 | 49 | 4.3 | 27.42 | 0.89621
2021-12-23 | 28.46 | 7.1 | 200 | 394 | 370 | 0.4 | 26 | 56 | 33 | 4.2 | 27.85 | 0.88226
2021-12-24 | 28.47 | 7.1 | 190 | 382 | 354 | 0.2 | 15 | 42 | 41 | 4 | 27.21 | 0.88257
2021-12-25 | 28.47 | 7.3 | 205 | 374 | 362 | 0.2 | 27 | 50 | 37 | 4.1 | 27.25 | 0.88257
2021-12-26 | 28.46 | 7.3 | 180 | 408 | 385 | 0.4 | 21 | 82 | 44 | 4.2 | 27.31 | 0.88226
2021-12-27 | 28.3 | 7.2 | 195 | 366 | 348 | 0.3 | 17 | 51 | 37 | 4 | 27.63 | 0.8773
2021-12-28 | 28.41 | 7.3 | 190 | 380 | 362 | 0.4 | 26 | 62 | 41 | 4.1 | 27.25 | 0.88071
2021-12-29 | 28.94 | 7.2 | 200 | 388 | 350 | 0.2 | 19 | 47 | 48 | 4.3 | 27.4 | 0.89714
2021-12-30 | 28.67 | 7.1 | 205 | 394 | 369 | 0.3 | 16 | 54 | 30 | 4.1 | 27.75 | 0.88877
2021-12-31 | 28.4 | 7.3 | 195 | 368 | 346 | 0.4 | 22 | 48 | 37 | 4.3 | 27.43 | 0.8804
| 875.4 | [10 empty] | 27.1374
STATE GANGA RIVER CONSERVATION AGENCY (DEPARTMENT OF URBAN DEVELOPMENT, UTTAR PRADESH)
Long-term Operation, Maintenance and Management of the Sewage Treatment System and Sewer network in the State of Uttar Pradesh {Package-8, Zone-Ghaziabad (UP)}
VA TECH WABAG LIMITED
LABORATORY LOG SHEETS-I
Name of the plant |  | Raw Sewage TSS: STP Plant Dundahera
Capacity |  | Raw Sewage TSS: 70 MLD
Technology |  | Raw Sewage TSS: SBR Based Technology
Month |  | Raw Sewage TSS: 2022-01-01
Date |  | Raw Sewage BOD: Raw Sewage; Raw Sewage COD: Final Outlet |  |  |  |  | Remarks
| INLET | OUTLET | pH | BOD | COD | TSS | DO | pH | BOD | COD | TSS | DO | OUTLET | Sludge Generation/Day
| MLD | MLD | ---- | mg/L | mg/L | mg/L | ppm | ---- | mg/L | mg/L | mg/L | ppm | MLD | MTM
2022-01-01 | 28.84 | 27.32 | 7.3 | 185 | 362 | 347 | 0.4 | 7.2 | 25 | 49 | 41 | 4.3 | 27.32 | 0.8652
2022-01-02 | 28.63 | 27.47 | 7.2 | 195 | 388 | 370 | 0.2 | 7.1 | 20 | 67 | 34 | 4.3 | 27.47 | 0.8589
2022-01-03 | 28.73 | 27.38 | 7 | 190 | 405 | 392 | 0.2 | 7.2 | 16 | 82 | 28 | 4 | 27.38 | 0.8619
2022-01-04 | 28.67 | 27.28 | 7.1 | 200 | 374 | 356 | 0.4 | 7 | 17 | 60 | 45 | 4.2 | 27.28 | 0.8601
2022-01-05 | 28.48 | 27.12 | 7.2 | 195 | 414 | 384 | 0.3 | 7.1 | 25 | 84 | 40 | 4.3 | 27.12 | 0.8544
2022-01-06 | 28.36 | 27.17 | 7.3 | 180 | 362 | 346 | 0.2 | 7.2 | 20 | 57 | 29 | 4.1 | 27.17 | 0.8508
2022-01-07 | 28.45 | 26.87 | 7.2 | 195 | 388 | 372 | 0.3 | 7.1 | 16 | 49 | 38 | 4.3 | 26.87 | 0.8535
2022-01-08 | 27.95 | 26.44 | 7.1 | 200 | 392 | 380 | 0.2 | 7 | 24 | 60 | 46 | 4 | 26.44 | 0.8385
2022-01-09 | 27.66 | 26.48 | 7.3 | 195 | 418 | 392 | 0.4 | 7.2 | 18 | 72 | 40 | 4.3 | 26.48 | 0.8298
2022-01-10 | 27.45 | 26.16 | 7.3 | 200 | 374 | 349 | 0.3 | 7.1 | 16 | 47 | 36 | 4.1 | 26.16 | 0.8235
2022-01-11 | 28.6 | 27.32 | 7.3 | 195 | 387 | 366 | 0.2 | 7.1 | 27 | 64 | 29 | 4.3 | 27.32 | 0.858
2022-01-12 | 27.46 | 26.15 | 7.4 | 180 | 410 | 374 | 0.4 | 7.3 | 20 | 80 | 41 | 4.1 | 26.15 | 0.8238
2022-01-13 | 27.46 | 26.28 | 7.3 | 190 | 372 | 348 | 0.3 | 7.2 | 16 | 59 | 37 | 4.2 | 26.28 | 0.8238
2022-01-14 | 28.47 | 27.38 | 7.4 | 195 | 390 | 361 | 0.3 | 7.3 | 19 | 70 | 28 | 4 | 27.38 | 0.8541
2022-01-15 | 28.46 | 26.95 | 7.1 | 185 | 365 | 346 | 0.2 | 7 | 15 | 52 | 39 | 4.1 | 26.95 | 0.8538
2022-01-16 | 28.93 | 27.64 | 7.3 | 200 | 408 | 370 | 0.4 | 7.2 | 21 | 74 | 45 | 4.3 | 27.64 | 0.8679
2022-01-17 | 28.56 | 27.31 | 7.2 | 180 | 381 | 348 | 0.2 | 7.3 | 16 | 52 | 34 | 4.1 | 27.31 | 0.8568
2022-01-18 | 28.67 | 27.43 | 7.4 | 195 | 388 | 364 | 0.2 | 7.2 | 19 | 66 | 42 | 4.3 | 27.43 | 0.8601
2022-01-19 | 28.57 | 27.54 | 7.3 | 200 | 400 | 378 | 0.4 | 7.1 | 24 | 78 | 30 | 4.3 | 27.54 | 0.8571
2022-01-20 | 28.45 | 27.28 | 7.2 | 190 | 372 | 354 | 0.3 | 7.1 | 18 | 54 | 41 | 4.2 | 27.28 | 0.8535
2022-01-21 | 28.87 | 27.63 | 7.4 | 185 | 380 | 369 | 0.4 | 7.3 | 15 | 61 | 39 | 4.4 | 27.63 | 0.8661
2022-01-22 | 28.93 | 27.69 | 7.2 | 190 | 372 | 355 | 0.2 | 7.1 | 21 | 74 | 28 | 4.1 | 27.69 | 0.8679
2022-01-23 | 28.63 | 27.37 | 7.1 | 200 | 405 | 370 | 0.3 | 7 | 17 | 87 | 44 | 4.4 | 27.37 | 0.8589
2022-01-24 | 28.52 | 27.34 | 7.3 | 185 | 364 | 352 | 0.4 | 7.2 | 23 | 53 | 39 | 4.2 | 27.34 | 0.8556
2022-01-25 | 28.57 | 27.28 | 7.2 | 195 | 387 | 360 | 0.2 | 7.1 | 27 | 48 | 30 | 4.3 | 27.28 | 0.8571
2022-01-26 | 28.56 | 27.36 | 7.4 | 180 | 370 | 348 | 0.3 | 7.3 | 20 | 51 | 44 | 4.1 | 27.36 | 0.8568
2022-01-27 | 28.57 | 27.32 | 7.2 | 200 | 382 | 362 | 0.4 | 7.1 | 25 | 68 | 34 | 4.2 | 27.32 | 0.8571
2022-01-28 | 28.59 | 27.56 | 7.3 | 185 | 371 | 341 | 0.2 | 7.2 | 17 | 55 | 30 | 4.3 | 27.56 | 0.8577
2022-01-29 | 28.53 | 27.19 | 7.2 | 200 | 400 | 367 | 0.3 | 7.1 | 24 | 62 | 42 | 4.1 | 27.19 | 0.8559
2022-01-30 | 28.46 | 27.38 | 7.4 | 190 | 430 | 392 | 0.4 | 7.3 | 15 | 88 | 39 | 4.4 | 27.38 | 0.8538
2022-01-31 | 28.84 | 27.51 | 7.2 | 185 | 370 | 350 | 0.2 | 7.1 | 21 | 52 | 47 | 4.2 | 27.51 | 0.8652
Total | 881.92 | [12 empty] | 26.4576