## Dhundhahera 56
STATE GANGA RIVER CONSERVATION AGENCY (DEPARTMENT OF URBAN DEVELOPMENT, UTTAR PRADESH)
Long-term Operation, Maintenance and Management of the Sewage Treatment System and Sewer network in the State of Uttar Pradesh {Package-8, Zone-Ghaziabad (UP)}
VA TECH WABAG LIMITED
LABORATORY LOG SHEETS-I
Name of the plant |  |  |  |  | STP Plant Dundahera
Capacity |  |  |  |  | 56 MLD
Technology |  |  |  |  | SBR Based Technology
Month |  |  |  |  | 2021-11-01
Date | Inlet Flow |  | Raw Sewage | [5 empty] | Final Outlet | [6 empty] | Remarks
|  | Outlet | pH | BOD (5 Days) | COD | TSS | DO | Faecal KL | pH | BOD (5 Days) | COD | TSS | DO | Slude Generation | Faecal Coliform (3 Days)
|  | MLD | ---- | mg/L | mg/L | mg/L | ppm | KL | ---- | mg/L | mg/L | mg/L | ppm | MTD | MPN
2021-11-01 | 25.34 | 24.26 | 7 | 190 | 362 | 341 | 0.2 | 185 | 6.8 | 5 | 20 | 7 | 5.1 | 1.0136 | 940
2021-11-02 | 25.55 | 24.43 | 7.2 | 185 | 377 | 356 | 0.4 | 195 | 7 | 9 | 15 | 4 | 5.3 | 1.022 | 860
2021-11-03 | 25.2 | 23.87 | 7.4 | 195 | 383 | 347 | 0.2 | 190 | 7.1 | 7 | 27 | 9 | 5.2 | 1.008 | 920
2021-11-04 | 25.64 | 24.53 | 7.2 | 180 | 390 | 360 | 0.3 | 170 | 6.9 | 4 | 16 | 5 | 5.4 | 1.0256 | 880
2021-11-05 | 25.08 | 23.84 | 7.3 | 185 | 363 | 343 | 0.4 | 195 | 7.1 | 8 | 24 | 8 | 5.1 | 1.0032 | 910
2021-11-06 | 25.43 | 24.32 | 7.3 | 195 | 389 | 371 | 0.4 | 169 | 7 | 6 | 19 | 7 | 5.4 | 1.0172 | 950
2021-11-07 | 25.55 | 24.45 | 7.1 | 175 | 373 | 354 | 0.3 | 175 | 6.8 | 9 | 24 | 6 | 5.2 | 1.022 | 790
2021-11-08 | 25.31 | 24.16 | 7.2 | 180 | 388 | 370 | 0.4 | 190 | 6.8 | 5 | 17 | 9 | 5.1 | 1.0124 | 830
2021-11-09 | 25.06 | 23.65 | 6.9 | 195 | 360 | 344 | 0.3 | 165 | 6.7 | 8 | 21 | 4 | 5.4 | 1.0024 | 890
2021-11-10 | 25.43 | 24.21 | 7.3 | 185 | 378 | 366 | 0.2 | 185 | 7.1 | 4 | 32 | 5 | 5.2 | 1.0172 | 940
2021-11-11 | 25.08 | 23.75 | 7.2 | 180 | 361 | 340 | 0.4 | 184 | 7 | 7 | 20 | 8 | 5.3 | 1.0032 | 810
2021-11-12 | 25.5 | 24.42 | 7.4 | 195 | 392 | 372 | 0.3 | 190 | 7.1 | 9 | 27 | 6 | 5.1 | 1.02 | 920
2021-11-13 | 25.27 | 24.16 | 7.3 | 175 | 373 | 354 | 0.2 | 185 | 7.1 | 5 | 18 | 9 | 5.2 | 1.0108 | 870
2021-11-14 | 25.03 | 23.68 | 7.4 | 180 | 386 | 370 | 0.4 | 190 | 7.2 | 6 | 29 | 7 | 5.1 | 1.0012 | 900
2021-11-15 | 25.55 | 24.36 | 7.2 | 195 | 368 | 342 | 0.3 | 175 | 7 | 4 | 20 | 5 | 5.3 | 1.022 | 870
2021-11-16 | 25.06 | 23.84 | 7.3 | 180 | 388 | 361 | 0.2 | 189 | 7.1 | 9 | 32 | 4 | 5.2 | 1.0024 | 910
2021-11-17 | 25.1 | 23.58 | 7 | 190 | 370 | 342 | 0.4 | 190 | 6.8 | 8 | 21 | 7 | 5.1 | 1.004 | 790
2021-11-18 | 25.31 | 24.25 | 7.2 | 175 | 378 | 364 | 0.3 | 189 | 7.1 | 5 | 30 | 8 | 5.3 | 1.0124 | 870
2021-11-19 | 25.22 | 23.63 | 7.2 | 185 | 362 | 340 | 0.2 | 189 | 7 | 7 | 21 | 5 | 5.1 | 1.0088 | 900
2021-11-20 | 25.17 | 23.85 | 7.1 | 180 | 384 | 361 | 0.4 | 195 | 6.8 | 4 | 32 | 7 | 5.2 | 1.0068 | 860
2021-11-21 | 25.1 | 23.93 | 7.3 | 195 | 396 | 372 | 0.4 | 193 | 7 | 9 | 46 | 8 | 5.1 | 1.004 | 910
2021-11-22 | 25.06 | 23.68 | 7.2 | 185 | 370 | 344 | 0.2 | 187 | 6.9 | 6 | 22 | 4 | 5.3 | 1.0024 | 820
2021-11-23 | 25.16 | 23.74 | 7.3 | 190 | 387 | 366 | 0.3 | 186 | 7 | 9 | 34 | 6 | 5.2 | 1.0064 | 910
2021-11-24 | 25.31 | 24.17 | 7.2 | 175 | 400 | 382 | 0.4 | 185 | 7 | 5 | 50 | 9 | 5 | 1.0124 | 870
2021-11-25 | 25.06 | 23.67 | 7.3 | 180 | 380 | 356 | 0.3 | 196 | 7.1 | 8 | 38 | 5 | 5.1 | 1.0024 | 940
2021-11-26 | 25.43 | 24.26 | 7.2 | 180 | 358 | 336 | 0.2 | 180 | 7 | 4 | 46 | 7 | 5.2 | 1.0172 | 930
2021-11-27 | 25.49 | 24.28 | 7.3 | 195 | 374 | 362 | 0.2 | 190 | 7.1 | 7 | 30 | 4 | 5 | 1.0196 | 870
2021-11-28 | 25.55 | 24.37 | 7.3 | 185 | 362 | 350 | 0.4 | 195 | 7.1 | 9 | 52 | 8 | 5.1 | 1.022 | 900
2021-11-29 | 25.55 | 24.41 | 7.2 | 180 | 385 | 368 | 0.3 | 198 | 7 | 5 | 39 | 6 | 5.2 | 1.022 | 890
2021-11-30 | 25.11 | 23.71 | 7.4 | 175 | 370 | 342 | 0.2 | 195 | 7.2 | 7 | 46 | 5 | 5.3 | 1.0044 | 810
| 758.7 | [6 empty] | 5600 | [5 empty] | 30.348
STATE GANGA RIVER CONSERVATION AGENCY (DEPARTMENT OF URBAN DEVELOPMENT, UTTAR PRADESH)
Long-term Operation, Maintenance and Management of the Sewage Treatment System and Sewer network in the State of Uttar Pradesh {Package-8, Zone-Ghaziabad (UP)}
VA TECH WABAG LIMITED
LABORATORY LOG SHEETS-I
Name of the plant |  |  |  | STP Plant Dundahera
Capacity |  |  |  | 56 MLD
Technology |  |  |  | SBR Based Technology
Month |  |  |  | 2021-12-01
Date |  | Raw Sewage | [5 empty] | Final Outlet | [7 empty] | Remarks
| INLET | pH | BOD (5 Days) | COD | TSS | DO | Faecal | pH | BOD (5 Days) | COD | TSS | OUTLET | DO | Sludge Generation/Day | Faecal Coliform (3 Days)
|  | ---- | mg/L | mg/L | mg/L | ppm | KL | ---- | mg/L | mg/L | mg/L | MLD | ppm | MTD | MPN
2021-12-01 | 28.32 | 7.2 | 190 | 371 | 354 | 0.3 | 168 | 7 | 7 | 40 | 9 | 27.43 | 5 | 0.8496 | 870
2021-12-02 | 28.78 | 7.1 | 175 | 366 | 341 | 0.4 | 170 | 6.9 | 5 | 32 | 5 | 27.64 | 5.1 | 0.8634 | 890
2021-12-03 | 27.34 | 7.3 | 190 | 388 | 362 | 0.2 | 162 | 7.1 | 9 | 46 | 4 | 26.21 | 5.2 | 0.8202 | 790
2021-12-04 | 28.41 | 7.2 | 185 | 370 | 349 | 0.3 | 145 | 7 | 6 | 38 | 7 | 27.47 | 5 | 0.8523 | 820
2021-12-05 | 28.39 | 7.3 | 180 | 392 | 370 | 0.4 | 146 | 7.1 | 8 | 54 | 9 | 27.63 | 5.1 | 0.8517 | 940
2021-12-06 | 28.38 | 7.2 | 195 | 377 | 354 | 0.2 | 187 | 7 | 4 | 46 | 6 | 27.46 | 5.2 | 0.8514 | 870
2021-12-07 | 28.59 | 7.1 | 175 | 360 | 340 | 0.3 | 186 | 6.9 | 9 | 32 | 4 | 27.4 | 5 | 0.8577 | 900
2021-12-08 | 27.32 | 7.3 | 180 | 381 | 361 | 0.2 | 185 | 7.1 | 7 | 50 | 7 | 27.35 | 5.3 | 0.8196 | 880
2021-12-09 | 27.91 | 7.3 | 195 | 355 | 336 | 0.4 | 194 | 7 | 4 | 31 | 5 | 26.81 | 5.1 | 0.8373 | 990
2021-12-10 | 28.56 | 7.1 | 185 | 372 | 351 | 0.3 | 185 | 6.9 | 6 | 56 | 8 | 27.47 | 5.2 | 0.8568 | 850
2021-12-11 | 28.47 | 7.3 | 180 | 380 | 342 | 0.2 | 184 | 7.1 | 8 | 29 | 6 | 27.56 | 5 | 0.8541 | 900
2021-12-12 | 28.37 | 7.2 | 195 | 394 | 374 | 0.4 | 190 | 7 | 9 | 48 | 8 | 27.52 | 5.3 | 0.8511 | 830
2021-12-13 | 28.73 | 7.4 | 175 | 381 | 358 | 0.3 | 185 | 7.2 | 7 | 35 | 4 | 27.61 | 5.1 | 0.8619 | 930
2021-12-14 | 28.3 | 7.3 | 195 | 350 | 339 | 0.4 | 190 | 7.1 | 8 | 23 | 7 | 27.46 | 5.3 | 0.849 | 890
2021-12-15 | 28.36 | 7.2 | 185 | 369 | 350 | 0.2 | 168.1 | 7.1 | 5 | 39 | 9 | 27.27 | 5.1 | 0.8508 | 910
2021-12-16 | 28.32 | 7.3 | 190 | 388 | 367 | 0.4 | 189 | 7.2 | 9 | 42 | 5 | 27.48 | 5.3 | 0.8496 | 950
2021-12-17 | 28.65 | 7.1 | 180 | 351 | 340 | 0.3 | 164 | 6.9 | 4 | 28 | 4 | 27.57 | 5 | 0.8595 | 870
2021-12-18 | 28.4 | 7.2 | 175 | 369 | 353 | 0.4 | 189 | 7 | 7 | 37 | 6 | 27.41 | 5.2 | 0.852 | 910
2021-12-19 | 28.53 | 7.3 | 185 | 390 | 371 | 0.2 | 168 | 7.1 | 5 | 58 | 9 | 27.48 | 5.3 | 0.8559 | 940
2021-12-20 | 28.34 | 7.2 | 195 | 362 | 345 | 0.3 | 170 | 7 | 8 | 40 | 7 | 27.26 | 5 | 0.8502 | 810
2021-12-21 | 28.73 | 7.1 | 190 | 376 | 358 | 0.4 | 177 | 7 | 6 | 37 | 5 | 27.71 | 5.2 | 0.8619 | 920
2021-12-22 | 28.76 | 7.3 | 175 | 352 | 337 | 0.2 | 162.4 | 7.1 | 8 | 24 | 8 | 27.6 | 5.3 | 0.8628 | 840
2021-12-23 | 27.95 | 7.1 | 190 | 387 | 362 | 0.4 | 146 | 6.9 | 9 | 40 | 6 | 26.58 | 5.1 | 0.8385 | 910
2021-12-24 | 27.56 | 7.1 | 185 | 370 | 346 | 0.2 | 185 | 7.1 | 4 | 29 | 9 | 26.54 | 5.3 | 0.8268 | 870
2021-12-25 | 27.35 | 7.3 | 195 | 366 | 358 | 0.2 | 178 | 7.1 | 7 | 38 | 5 | 26.21 | 5.1 | 0.8205 | 900
2021-12-26 | 28.4 | 7.3 | 175 | 392 | 377 | 0.4 | 180 | 7.2 | 4 | 42 | 8 | 28.54 | 5 | 0.852 | 940
2021-12-27 | 27.25 | 7.2 | 190 | 355 | 340 | 0.3 | 190 | 7 | 9 | 26 | 4 | 26.22 | 5.2 | 0.8175 | 970
2021-12-28 | 27.82 | 7.3 | 185 | 374 | 357 | 0.4 | 170 | 7.1 | 6 | 34 | 7 | 26.61 | 5.2 | 0.8346 | 880
2021-12-29 | 28.67 | 7.2 | 195 | 368 | 343 | 0.2 | 198 | 7 | 5 | 28 | 9 | 27.84 | 5.3 | 0.8601 | 900
2021-12-30 | 28.8 | 7.1 | 200 | 380 | 362 | 0.3 | 170 | 6.9 | 7 | 41 | 6 | 27.63 | 5 | 0.864 | 910
2021-12-31 | 28.34 | 7.3 | 190 | 358 | 339 | 0.4 | 196 | 7.1 | 4 | 36 | 8 | 27.43 | 5.3 | 0.8502 | 950
Total | 876.1 | [5 empty] | 5477.5 | [6 empty] | 26.283
STATE GANGA RIVER CONSERVATION AGENCY (DEPARTMENT OF URBAN DEVELOPMENT, UTTAR PRADESH)
Long-term Operation, Maintenance and Management of the Sewage Treatment System and Sewer network in the State of Uttar Pradesh {Package-8, Zone-Ghaziabad (UP)}
VA TECH WABAG LIMITED
LABORATORY LOG SHEETS-I
Name of the plant |  |  |  | STP Plant Dundahera
Capacity |  |  |  | 56 MLD
Technology |  |  |  | SBR Based Technology
Month |  |  |  | 2022-01-01
Date |  | Raw Sewage | [5 empty] | Final Outlet | [7 empty] | Remarks
| INLET | pH | BOD (5 Days) | COD | TSS | DO | Faecal | pH | BOD (5 Days) | COD | TSS | DO | Faecal Coliform (3 Days) | OUTLET | Sludge Generation/Day
| MLD | ---- | mg/L | mg/L | mg/L | ppm | KL | ---- | mg/L | mg/L | mg/L | ppm | MPN | MLD | MTD
2022-01-01 | 28.95 | 7.3 | 175 | 355 | 340 | 0.4 | 170 | 7.1 | 8 | 32 | 8 | 5.2 | 870 | 27.34 | 0.8685
2022-01-02 | 28.76 | 72 | 190 | 376 | 362 | 0.2 | 177 | 7 | 5 | 46 | 4 | 5.2 | 900 | 27.58 | 0.8628
2022-01-03 | 28.54 | 7.3 | 185 | 384 | 387 | 0.2 | 162.4 | 7.1 | 7 | 62 | 6 | 5.3 | 950 | 27.64 | 0.8562
2022-01-04 | 28.61 | 7.1 | 195 | 368 | 348 | 0.4 | 146 | 6.9 | 5 | 36 | 9 | 5.1 | 890 | 27.45 | 0.8583
2022-01-05 | 28.73 | 7.2 | 190 | 390 | 372 | 0.2 | 185 | 7 | 8 | 48 | 7 | 5.3 | 920 | 27.56 | 0.8619
2022-01-06 | 28.46 | 7.3 | 175 | 354 | 338 | 0.3 | 178 | 6.9 | 9 | 30 | 5 | 5 | 900 | 27.16 | 0.8538
2022-01-07 | 28.67 | 7.2 | 185 | 378 | 360 | 0.3 | 180 | 7.1 | 6 | 26 | 8 | 5.2 | 950 | 27.82 | 0.8601
2022-01-08 | 28.45 | 7.1 | 190 | 386 | 374 | 0.2 | 190 | 7 | 4 | 39 | 4 | 5.1 | 970 | 27.51 | 0.8535
2022-01-09 | 28.47 | 7.3 | 185 | 400 | 386 | 0.4 | 170 | 7.1 | 7 | 48 | 9 | 5.2 | 920 | 27.39 | 0.8541
2022-01-10 | 28.75 | 7.3 | 185 | 368 | 342 | 0.3 | 198 | 7 | 9 | 30 | 6 | 5.3 | 950 | 26.64 | 0.8625
2022-01-11 | 28.48 | 7.2 | 190 | 381 | 358 | 0.2 | 170 | 7 | 6 | 42 | 5 | 5 | 900 | 27.43 | 0.8544
2022-01-12 | 28.36 | 7.4 | 175 | 388 | 369 | 0.4 | 196 | 7.2 | 8 | 58 | 7 | 5.2 | 930 | 27.32 | 0.8508
2022-01-13 | 28.62 | 7.3 | 185 | 361 | 340 | 0.3 | 185 | 7.1 | 5 | 41 | 4 | 5.3 | 970 | 27.73 | 0.8586
2022-01-14 | 28.73 | 7.4 | 190 | 384 | 352 | 0.3 | 190 | 7.2 | 4 | 32 | 8 | 5.1 | 900 | 27.31 | 0.8619
2022-01-15 | 28.73 | 7.1 | 180 | 350 | 338 | 0.2 | 168.1 | 6.9 | 7 | 28 | 6 | 5.2 | 950 | 27.74 | 0.8619
2022-01-16 | 28.43 | 7.3 | 195 | 388 | 364 | 0.4 | 189 | 7.1 | 9 | 49 | 9 | 5 | 860 | 27.88 | 0.8529
2022-01-17 | 28.56 | 7.2 | 175 | 364 | 340 | 0.3 | 180.5 | 7 | 6 | 26 | 7 | 5.3 | 910 | 27.34 | 0.8568
2022-01-18 | 28.72 | 7.4 | 190 | 380 | 358 | 0.2 | 189 | 7.2 | 5 | 34 | 4 | 5.1 | 880 | 27.62 | 0.8616
2022-01-19 | 28.52 | 7.3 | 190 | 389 | 372 | 0.4 | 175 | 7.1 | 9 | 42 | 9 | 5.3 | 850 | 27.73 | 0.8556
2022-01-20 | 28.73 | 7.2 | 185 | 360 | 346 | 0.3 | 180 | 7 | 4 | 22 | 5 | 5 | 920 | 27.62 | 0.8619
2022-01-21 | 28.57 | 7.4 | 175 | 378 | 364 | 0.4 | 170 | 7.2 | 7 | 37 | 6 | 5.2 | 960 | 27.58 | 0.8571
2022-01-22 | 28.44 | 7.2 | 180 | 366 | 341 | 0.2 | 175 | 7 | 6 | 48 | 7 | 5.4 | 910 | 27.84 | 0.8532
2022-01-23 | 28.56 | 7.1 | 195 | 389 | 364 | 0.3 | 180 | 6.9 | 8 | 56 | 9 | 5.2 | 900 | 27.64 | 0.8568
2022-01-24 | 28.68 | 7.3 | 180 | 352 | 340 | 0.4 | 185 | 7.1 | 5 | 31 | 6 | 5.3 | 820 | 27.32 | 0.8604
2022-01-25 | 28.52 | 7.2 | 190 | 376 | 352 | 0.2 | 187 | 7 | 4 | 28 | 4 | 5.1 | 870 | 27.49 | 0.8556
2022-01-26 | 27.38 | 7.4 | 175 | 358 | 340 | 0.3 | 186 | 7.2 | 7 | 30 | 5 | 5.4 | 860 | 26,52 | 0.8214
2022-01-27 | 28.37 | 7.2 | 195 | 370 | 355 | 0.4 | 185 | 7 | 9 | 42 | 7 | 5.2 | 900 | 27.35 | 0.8511
2022-01-28 | 28.44 | 7.3 | 180 | 350 | 339 | 0.2 | 194 | 7.1 | 5 | 27 | 9 | 5.4 | 950 | 27.45 | 0.8532
2022-01-29 | 28.41 | 7.2 | 195 | 382 | 361 | 0.3 | 185 | 7 | 6 | 39 | 6 | 5.1 | 920 | 27.37 | 0.8523
2022-01-30 | 28.73 | 7.4 | 185 | 396 | 384 | 0.4 | 184 | 7.2 | 4 | 47 | 9 | 5.3 | 830 | 27.43 | 0.8619
2022-01-31 | 28.76 | 7.2 | 175 | 360 | 342 | 0.2 | 190 | 7 | 7 | 30 | 5 | 5.1 | 790 | 27.58 | 0.8628
Total | 885.13 | [5 empty] | 5600 | [7 empty] | 26.5539